## Chemical Feed Calculator
TriCleanAir Formula-AS-TCA Calculator
Change the yellow input cells. All chemical-feed and diluted-solution rates update automatically. |  |  |  | DOSAGE REFERENCE | Neat chemical | Diluted solution | Diluted solution
|  |  |  | Dose (ppm) | mL/hr | mL/hr | gal/day
INPUTS | Value | Units | Description | 1 | 10.1379 | 48.5141 | 0.30759
Feed-water flow | 48.43 | GPM | Pure + Reject Water = | 2 | 20.2759 | 97.0283 | 0.61517
Desired dosage | 5 | ppm | Target Dosage | 3 | 30.4138 | 145.5424 | 0.92276
Formula-AS-TCA | 4000 | mL | Chemical used in each dilution batch | 4 | 40.5517 | 194.0566 | 1.2303
Dilution water | 4 | US gal | Water added to the chemical | 5 | 50.6896 | 242.5707 | 1.5379
Chemical specific gravity | 1.085 | SG | DO NOT CHANGE | 6 | 60.8276 | 291.0849 | 1.8455
Operating time | 24 | hr/day | Daily system operating hours | 7 | 70.9655 | 339.599 | 2.1531
|  |  |  | 8 | 81.1034 | 388.1132 | 2.4607
CALCULATED RESULTS | Result | Units | Formula basis | 9 | 91.2413 | 436.6273 | 2.7683
Feed-water volume | 69739.2 | gal/day | Flow × 60 × operating hours | 10 | 101.3793 | 485.1415 | 3.0759
Feed-water volume | 10999.6496 | L/hr | Flow × 3.785411784 × 60
Required neat chemical | 50.6896 | mL/hr | ppm × L/hr ÷ density conversion
Required neat chemical per day | 41.1365 | fl oz/day | Neat mL/hr converted to fl oz/day
Required neat chemical per year | 117.3033 | gal/year | Neat mL/hr converted to gal/year
Dilution-water volume | 15141.6471 | mL | Dilution gallons × 3,785.411784
Total mixed-solution volume | 19141.6471 | mL | Chemical mL + dilution-water mL
Chemical fraction in mixed solution | 20.9% | % | Chemical volume ÷ total solution volume
Diluted-solution pump rate | 242.5707 | mL/hr | Neat rate ÷ chemical fraction
Diluted-solution pump rate | 4.0428 | mL/min | Diluted mL/hr ÷ 60
Diluted solution per day | 5.8217 | L/day | Diluted mL/hr × operating hours ÷ 1,000
Diluted solution per day | 1.5379 | gal/day | Diluted mL/hr × operating hours ÷ 3,785.411784
One batch lasts | 78.9116 | hours | Total batch volume ÷ diluted pump rate
Dosing Pump - DMS200 | 4.851% | P
Dosing Pump - AKS500 | 16.17% | P